## 200 Spec
| Model Suffix | -221XX | -224XX | -225XX
Performance
Cooling Capacity - (BTU/H) See Note 1 |  | 21000
Power Requirements (Volts/Phase/Hertz) |  | 208-230/1/60
Current Draw (Amps) |  | 19
Circuit Size (Amps) |  | 30
Sound Characteristic dB(A) See Note 2 |  | 0 - 4
Controls
Type |  | Thermostat | PID
Accuracy |  | ± 2°F | ± 0.5°F
Optional Remote Sensor |  | Yes | Standard
Evaporator Section
Fan Motor Size (HP) |  | 1/4
Air Flow (CFM) |  | 300 - 800
External Static Pressure (inches WG) |  | 0.1"
Condensate Drain |  | 1/2" O.D.
Condenser Section
Flow Rate (GPM) |  | 2.0 - 5.0
Water Temperature (Maximum, °F ) |  | 85
Water Side Pressure Drop (psi) |  | 0.8 - 3.4
Piping Connections |  | 0.750" O.D.
Electric Reheat
Capacity |  | N/A | 1kW | 2kW
Power Requirements (Volts/Phase/Hertz) |  | N/A | 208-230/1/60 | 208-230/1/60
Current Draw (Amps) See Note 3 |  | N/A | 5.1 | 9.6
Humidifier
Accuracy |  | ± 5%
Capacity |  | 5 pounds/hour
Power Requirements (Volts/Phase/Hertz) |  | 208-230/1/60
Current Draw (Amps) See Note 4 |  | 10
Cabinet
Construction |  | .063 Aluminum
Finish |  | Blue, Powder Coat, Corrosion Inhibiting
Weight (pounds) |  | 225-250
Dimensions (Inches) | Length | 47.5
| Width | 23.5
| Height | 18.25
Suspension |  | Upper corners, 3/8" x #16 Threaded Rod
Agency Approval(s) |  | ETL IAW UL/CSA 1995
1. Cooling capacity rating conditions: 75F/50% RH evaporator, 95F condenser.
2. Sound data shows increase over fan filter unit noise. Readings taken 30" from face of fan filter unit.
3. 2kW requires additional power circuit
4. Requires additional power circuit, water supply, and drain
HEPAir reserves the right to make changes to this document without prior notice at our sole discretion.

## 088 Spec
| Model Suffix | -221XX | -224XX | -225XX
Performance
Cooling Capacity - (BTU/H) See Note 1 |  | 9050 / 10200
Power Requirements (Volts/Phase/Hertz) |  | 208-230/1/60
Current Draw (Amps) |  | 8.8
Circuit Size (Amps) |  | 20
Sound Characteristic dB(A) See Note 2 |  | 0 - 4
Controls
Type |  | Thermostat | PID
Accuracy |  | ± 2°F | ± 0.5°F
Optional Remote Sensor |  | Yes | Standard
Evaporator Section
Fan Motor Size (HP) |  | 1/4
Air Flow (CFM) |  | 150 - 800
External Static Pressure (inches WG) |  | 0.1"
Condensate Drain |  | 0.500" O.D.
Condenser Section
Flow Rate (GPM) |  | 1.0 - 2.5
Water Temperature (Maximum, °F ) |  | 85
Water Side Pressure Drop (psi) |  | 0.8 - 3.4
Piping Connections |  | 0.500" O.D.
Electric Reheat
Capacity |  | N/A | 1kW | 2kW
Power Requirements (Volts/Phase/Hertz) |  | N/A | 208-230/1/60 | 208-230/1/60
Current Draw (Amps) See Note 4 |  | N/A | 5.1 | 9.6
Humidifier
Accuracy |  | ± 5%
Capacity |  | 5 pounds/hour
Power Requirements (Volts/Phase/Hertz) |  | 208-230/1/60
Current Draw (Amps) See Note 3 |  | 10
Cabinet
Construction |  | .063 Aluminum
Finish |  | Blue, Powder Coat, Corrosion Inhibiting
Weight (pounds) |  | 175-200
Dimensions (Inches) | Length | 47.5
| Width | 23.5
| Height | 14.25
Suspension |  | Upper corners, 3/8" x #16 Threaded Rod
Agency Approval(s) |  | ETL IAW UL/CSA 1995
1. Cooling capacity rating conditions: 75F/50% RH evaporator, 95F condenser / 85F/35% RH evaporator, 95F condenser
2. Sound data shows increase over fan filter unit noise. Readings taken 30" from face of fan filter unit.
3. 2kW requires additional power circuit
4. Requires additional power circuit, water supply, and drain
HEPAir reserves the right to make changes to this document without prior notice at our sole discretion.

## 050 Spec
| Model Suffix | -121XX | -125XX
Performance
Cooling Capacity - (BTU/H) See Note 1 |  | 7,400 / 8700
Power Requirements (Volts/Phase/Hertz) |  | 115/1/60
Current Draw (Amps) |  | 13.9
Circuit Size (Amps) |  | 20
Sound Characteristic dB(A) See Note 2 |  | 0 - 4
Controls
Type |  | Thermostat | PID
Accuracy |  | ± 2°F | ± 0.5°F
Optional Remote Sensor |  | Yes | Standard
Evaporator Section
Fan Motor Size (HP) |  | 1/4
Air Flow (CFM) |  | 150 - 800
External Static Pressure (inches WG) |  | 0.1"
Drain (Optional) |  | 0.500" O.D.
Condenser Section
Flow Rate (GPM) |  | 1.0 - 2.0
Water Temperature (Maximum, °F ) |  | 85
Water Side Pressure Drop (psi) |  | 0.5 - 1.5
Piping Connections |  | 0.500" O.D.
Electric Reheat
Capacity |  | N/A | 0.6kW
Power Requirements (Volts/Phase/Hertz) |  | N/A | 115/1/60
Current Draw (Amps) See Note 3 |  | N/A | 5.2
Humidifier
Accuracy |  | ± 5%
Capacity |  | 5 pounds/hour
Power Requirements (Volts/Phase/Hertz) |  | 208-230/1/60
Current Draw (Amps) See Note 4 |  | 10
Cabinet
Construction |  | .063 Aluminum
Finish |  | Blue, Powder Coat, Corrosion Inhibiting
Weight (pounds) |  | 175 -200
Dimensions (Inches) | Length | 47.5
| Width | 23.5
| Height | 14.25
Suspension |  | Upper corners, 3/8" x #16 Threaded Rod
Agency Approval(s) |  | ETL IAW UL/CSA 1995
1. Cooling capacity rating conditions: 75F/50% RH evaporator, 95F condenser / 85F/35% RH evaporator, 95F condenser
2. Sound data shows increase over fan filter unit noise. Readings taken 30" from face of fan filter unit.
3. Requires additional power circuit
4. Requires additional power circuit, water supply, and drain
HEPAir reserves the right to make changes to this document without prior notice at our sole discretion.

## Electrical
Model | Voltage | Unit Amps | Heater Amps | Total Amps | Minimum Circuit | 20 Amp Circuits | 30 Amp Circuits
24W050-121XX | 115/1/60 | 13.9 |  | 13.9 | 17.375 | 1
24W050-125XX | 115/1/60 | 13.9 | 5.2 | 19.1 | 23.875 | 2 | 1
24W088-221XX | 208/1/60 | 8.8 |  | 8.8 | 11 | 1
24W088-224XX | 208/1/60 | 8.8 | 5.1 | 13.9 | 17.375 | 1
24W088-225XX | 208/1/60 | 8.8 | 9.6 | 18.4 | 23 | 2 | 1
Notes: | Minimum circuit load calculated IAW ETL guidelines, but local codes may apply
Humidifier voltage is 208/1/60, 10 amps

## Condesnser
TD | Flow Rate | Heat Rejection
20 | 0.6 | 5
| 0.8 | 6
| 1 | 6.8
| 1.2 | 7.6
| 1.4 | 8.3
| 1.6 | 9.1
| 1.8 | 9.8
| 2 | 10.3
| 2.2 | 10.9
| 2.4 | 11.4
| 2.6 | 11.7
| 2.8 | 12
| 3 | 12.2
25 | 0.6 | 6.6
| 0.8 | 7.8
| 1 | 8.9
| 1.2 | 10
| 1.4 | 11
| 1.6 | 11.9
| 1.8 | 12.8
| 2 | 13.5
| 2.2 | 14.2
| 2.4 | 15
| 2.6 | 15.5
| 2.8 | 16
| 3 | 16.4
30 | 0.6 | 7.3
| 0.8 | 9
| 1 | 10.6
| 1.2 | 12
| 1.4 | 13.5
| 1.6 | 14.8
| 1.8 | 16
| 2 | 17
| 2.2 | 18
| 2.4 | 18.8
| 2.6 | 19.5
| 2.8 | 20.1
| 3 | 20.7

## 050 WC Performance
Evaporator Entering Air Dry Bulb Temperature, ºF
Evaporator | Evaporator | 65ºF |  | 75ºF |  | 85ºF
Air Flow | Entering RH% | Sensible BTUH | Latent BTUH | Sensible BTUH | Latent BTUH | Sensible BTUH | Latent BTUH
300 cfm | 35% | 5050 | 0 | 6300 | 0 | 7200 | 0
| 40% | 5050 | 0 | 6300 | 0 | 7200 | 0
| 45% | 5050 | 0 | 6300 | 0 | 7200 | 0
| 50% | 5050 | 0 | 6200 | 250 | 6800 | 600
| 55% | 5050 | 0 | 6050 | 500 | 6550 | 1200
550 cfm | 35% | 6100 | 0 | 7200 | 0 | 8200 | 0
| 40% | 6100 | 0 | 7200 | 0 | 8200 | 0
| 45% | 6100 | 0 | 7200 | 0 | 8200 | 0
| 50% | 6100 | 0 | 7200 | 0 | 8200 | 0
| 55% | 6100 | 0 | 7200 | 0 | 8200 | 0
800 cfm | 35% | 6400 | 0 | 7400 | 0 | 8700 | 0
| 40% | 6400 | 0 | 7400 | 0 | 8700 | 0
| 45% | 6400 | 0 | 7400 | 0 | 8700 | 0
| 50% | 6400 | 0 | 7400 | 0 | 8700 | 0
| 55% | 6400 | 0 | 7400 | 0 | 8700 | 0

## 088 WC Performance
Evaporator Entering Air Dry Bulb Temperature, ºF
Evaporator | Evaporator | 65ºF |  | 75ºF |  | 85ºF
Air Flow | Entering RH% | Sensible BTUH | Latent BTUH | Sensible BTUH | Latent BTUH | Sensible BTUH | Latent BTUH
150 cfm | 35% | 5400 | 750 | 6000 | 1300 | 6450 | 2050
| 40% | 5250 | 1100 | 5750 | 1750 | 6100 | 2600
| 45% | 5100 | 1400 | 5500 | 2200 | 5800 | 3200
| 50% | 4900 | 1800 | 5250 | 2750 | 5550 | 3750
| 55% | 4750 | 2100 | 5000 | 330 | 5250 | 4300
300 cfm | 35% | 6700 | 0 | 7700 | 0 | 8700 | 0
| 40% | 6550 | 300 | 7500 | 400 | 8300 | 800
| 45% | 6400 | 550 | 7300 | 900 | 7900 | 1600
| 50% | 6200 | 1000 | 6900 | 1550 | 7400 | 2500
| 55% | 6000 | 1400 | 6450 | 2250 | 6850 | 3250
550 cfm | 35% | 7900 | 0 | 9050 | 0 | 10200 | 0
| 40% | 7900 | 0 | 9050 | 0 | 10200 | 0
| 45% | 7900 | 0 | 9050 | 0 | 10200 | 0
| 50% | 7900 | 0 | 8950 | 300 | 9950 | 600
| 55% | 7900 | 0 | 8900 | 600 | 9600 | 1200
800 cfm | 35% | 7900 | 0 | 9050 | 0 | 10200 | 0
| 40% | 7900 | 0 | 9050 | 0 | 10200 | 0
| 45% | 7900 | 0 | 9050 | 0 | 10200 | 0
| 50% | 7900 | 0 | 9050 | 0 | 10200 | 0
| 55% | 7900 | 0 | 9050 | 0 | 10200 | 0

## 200 WC Performance
Evaporator Entering Air Dry Bulb Temperature, ºF
Evaporator | Evaporator | 65ºF |  | 75ºF |  | 85ºF
Air Flow | Entering RH% | Sensible BTUH | Latent BTUH | Sensible BTUH | Latent BTUH | Sensible BTUH | Latent BTUH
300 cfm | 35% | 7800 | 0 | 11300 | 2100 | 13500 | 2700
| 40% | 7500 | 0 | 11300 | 4000 | 12500 | 5500
| 45% | 7300 | 600 | 10700 | 4300 | 11800 | 6600
| 50% | 7000 | 1200 | 10500 | 5100 | 11300 | 7700
| 55% | 6800 | 3000 | 9300 | 5500 | 10900 | 9100
550 cfm | 35% | 14900 | 0 | 17500 | 900 | 19900 | 1200
| 40% | 14900 | 0 | 16300 | 2100 | 18100 | 3900
| 45% | 14500 | 1000 | 15500 | 3400 | 16900 | 6800
| 50% | 13300 | 2500 | 15100 | 5100 | 16000 | 7500
| 55% | 12500 | 4300 | 13000 | 5700 | 14300 | 8300
800 cfm | 35% | 17700 | 0 | 21600 | 600 | 22500 | 1600
| 40% | 17700 | 0 | 20000 | 1300 | 20700 | 1800
| 45% | 17300 | 0 | 19000 | 2700 | 19000 | 3500
| 50% | 16700 | 2500 | 17900 | 3000 | 17300 | 5500
| 55% | 15900 | 5500 | 15500 | 3300 | 15500 | 7700